## PumpStation
Project: Storm Design
| STORM PUMP STATION (C3) |  |  |  | INSTRUCTIONS: Insert the values in red highlights
DESIGN INPUT DATA | [5 empty] | DATA: | Insert the values in red highlights
| Pump Station capacity |  | 4630 | l/sec
| Pump Station ground level |  | 38.3 | m | RSULTS: | The yellow highlighted are results
| Max. level of force main |  | 41.6 | m
| Inlet pipe invert level |  | 33.23 | m
| Water level at the last manhole |  | 34.7 | m
| Inlet pipe diameter |  | - | m | 1.2
| No.of force maine pipe |  | 1 | No.
| Force maine length (for each) |  | 370 | m
| Force main material | D.C.I.
| C : Friction Factor …. New / Old | 140 | 120 | ----
PUMP SELECTION
| Total No. of pumps |  | 4 | nos.
| Duty No. of pumps |  | 3 | nos.
| Stand-by No. of pumps |  | 1 | nos.
| Calculated pump capacity |  | 1543.3333 | l/sec
| Selected pump capacity |  | 1543.3333 | l/sec
SUMP DESIGN
1- Sump design(wet well for each set of pump)
| Pump capacity |  | 1543.3333 | l/sec
| Qout |  | 4630 | l/sec
| Proposed No. of starts per hour |  | 6 | nos.
| Calculated cycle duration(T) |  | 10 | min.
| Min. Required Sump volume(V) =Q*T/4 |  | 694.5 | m3
| Proposed sump Length (L) |  | 17 | m
| Proposed sump Width (W) |  | 12.6 | m
| Calculated sump Area |  | 214.2 | m2
| Calculated storage depth (h) |  | 3.2423 | m
[5 empty] | v min-max (m/s): | #REF!
3- SUMP LEVELING
| Pump Station ground level |  | 38.3 | m
| Inlet pipe invert level |  | 33.23 | m
| High Water Alarm level |  | 34.9 | m
| Max. Water level = Start level of pump No. 3 |  | 34.7 | m | 2.1
| Start level of pump No. 2 |  | 33.6192 | m
| Start level of pump No. 1 |  | 32.5385 | m
| all pumps stop level |  | 31.4577 | m
| submergence height (As per manufacture recommendations) |  | 1.5 | m
| Pump suction bell level |  | 29.9577 | m | 0.3D - 0.5D
| Space below the pump eye (As per manufacture recommendations) |  | 0.6 | m
| Selected bottom level |  | 29.3577 | m
| Total Sump depth |  | 8.9423 | m
PIPING SIZING
| 1- DELIVERY BRANCH SIZING |  |  |  | CHECK: Discharge pipe velocity
| Pump capacity |  | 1543.3333 | l/sec | Para. 8.1.3 FHA, HEC24
| Delivery pipe diameter |  | 0.9 | m | v min-max (m/s):
| Velocity |  | 2.4272 | m/sec | CHECK
OK
2- HEADER BRANCH SIZING
| Pump capacity |  | 4630 | l/sec
| Header branch pipe diameter |  | 1.4 | m
| Velocity |  | 3.0092 | m/sec | CHECK
OK
3- FORCE MAIN SIZING
| Pump capacity |  | 4630 | l/sec
| Force main diameter |  | 1.4 | m
| Velocity |  | 3.0092 | m/sec | CHECK
OK
PUMP HEAD CLCULATIONS
Piping head losses '' Hf '' can be calculated according to HAZEN WILLIAMS equation
Where,
Hf : Pipe friction loss
Q : Flow rate
C : HAZEN WILLIAMS Coefficient
L : Pipe length
D : Pipe diameter
' K '' VALUE FOR VALVE AND PIPE FITTINGS ON EACH PIPE SECTOR
| PIPE SECTOR | K | DELIVERY BRACH K1 | MAIN HEADER K1
| Elbow 90O, standard | 0.75 | 1 | 0
| Non Return valve | 2 | 1 | 0
| Dismantling joint | 0.1 | 1 | 2
| Gate valve | 0.2 | 1 | 1
| TEE, branch flow | 1 | 1 | 1
| TEE, in line | 0.4 | 0 | 4
| Total (K) value |  | 4.05 | 3
1 - DELIVERY BRANCH HEAD LOSSES
| Pump capacity |  | 1543.3333 | l/sec | CHECK: Discharge pipe velocity
| Diameter |  | 0.9 | m | Para. 8.1.3 FHA, HEC24
| Delivery pipe length |  | 10 | m | v min-max (m/s): | 1-3 | AECOM can accept 3.50m/s
| Velocity |  | 2.4272 | m/sec | CHECK
| Total friction coefficient ''K'' |  | 4.05 | -- | OK
| Total minor losses ( k * V2/2g ) |  | 1.2161 | m
| Total friction losses |  | 0.056646 | m
| Total head losses through delivery branch |  | 1.2727 | m
2 - HEADER BRANCH HEAD LOSSES
| Pump capacity |  | 4630 | l/sec | CHECK: Discharge pipe velocity
| Diameter |  | 1.4 | m | Para. 8.1.3 FHA, HEC24
| Header branch pipe length |  | 20 | m | v min-max (m/s):
| Velocity |  | 3.0092 | m/sec | CHECK
| Total friction coefficient ''K'' |  | 3 | -- | OK
| Total minor losses ( k * V2/2g ) |  | 1.3846 | m
| Total friction losses |  | 0.10055 | m
| Total head losses through Header branch |  | 1.4852 | m
3 - FORCE MAIN HEAD LOSSES
| Pump station capacity |  | 4630 | l/sec | CHECK: Discharge pipe velocity
| Diameter |  | 1.4 | m | Para. 8.1.3 FHA, HEC24
| Force main length |  | 370 | m | v min-max (m/s):
| Velocity |  | 3.0092 | m/sec | CHECK
| Total friction losses (OLD PIPE) |  | 1.8602 | m | OK
| Total friction losses (NEW PIPE) |  | 1.3987 | m
| Total Force Main minor losses= (40% of total friction losses ) |  | 0.74408 | m
| Total head losses through Force main |  | 2.6043 | m
4 - STATIC HEAD CALCULATION
| Sump min. water level |  | 31.4577 | m
| Max. level along Force Main pipe |  | 41.6 | m
| STATIC HEAD |  | 10.1423 | m
5 - TOTAL HEAD LOSSES CALCULATION
| Total head losses |  | 5.3622 | m | Usually 30% can be taken
| Static Head as mention in hydraulic calculation |  | 10.1423 | m
| Calculated Pump Head |  | 15.5045 | m
| Selected Pump Head |  | 16 | m
6 - PUMP DATA
| Pump Capacity |  | 1543.3333 | l/sec
| Pump Head |  | 16 | m
PUMP STATION SUMMARY
| Total Sump depth |  | 8.9423 | m
| FORCE MAIN DIAMETER INSIDE PUMP STATION (INNER) |  | 1400 | mm
| DUTY NO. OF PUMPS |  | 3 | nos.
| STAND-BY NO. OF PUMPS |  | 1 | nos.
| TOTAL NO OF PUMPS |  | 4 | nos.
| PUMP CAPACIT- for each |  | 1543.3333 | l/sec
| PUMP HEAD |  | 16 | m
| DENSITY OF LIQUID |  | 1 | kg/l
| PUMP HYDRAULIC POWER (PH) |  | 242.2416 | kW
| Pump Efficiency (nP) |  | 80 | %
| MOTOR/PUMP SHAFT Power (ps) |  | 302.802 | kW
| MOTOR EFFICIENCY (nM) |  | 90 | %
| SAFETY MARGIN |  | 1.15
| REQUIRED MOTOR SIZE (kW) |  | 386.9137 | kW
| REQUIRED MOTOR SIZE (HP) |  | 519 | HP

## LiquidsDensity
Liquid | Tem(°C) | Density(Kg/m3)
Acetic Acid | 25 | 1049
Acetone | 25 | 784.6
Acetonitrile | 20 | 782
Alcohol, ethyl (ethanol) | 25 | 785.1
Alcohol, methyl (methanol) | 25 | 786.5
Alcohol, propyl | 25 | 800
Ammonia (aqua) | 25 | 823.5
Aniline | 25 | 1019
Automobile oils | 15 | 880 - 940
Beer (varies) | 10 | 1010
Benzene | 25 | 873.8
Benzil | 15 | 1230
Brine | 15 | 1230
Bromine | 25 | 3120
Butyric Acid | 20 | 959
Butane | 25 | 599
n-Butyl Acetate | 20 | 880
n-Butyl Alcohol | 20 | 810
n-Butylhloride | 20 | 886
Caproic acid | 25 | 921
Carbolic acid | 15 | 956
Carbon disulfide | 25 | 1261
Carbon tetrachloride | 25 | 1584
Carene | 25 | 857
Castor oil | 25 | 956.1
Chloride | 25 | 1560
Chlorobenzene | 20 | 1106
Chloroform | 20 | 1489
Chloroform | 25 | 1465
Citric acid | 25 | 1660
Coconut oil | 15 | 924
Cotton seed oil | 15 | 926
Cresol | 25 | 1024
Creosote | 15 | 1067
Crude oil, 48o API | 60oF | 790
Crude oil, 40o API | 60oF | 825
Crude oil, 35.6o API | 60oF | 847
Crude oil, 32.6o API | 60oF | 862
Crude oil,alifornia | 60oF | 915
Crude oil, Mexican | 60oF | 973
Crude oil, Texas | 60oF | 873
Cumene | 25 | 860
Cyclohexane | 20 | 779
Cyclopentane | 20 | 745
Decane | 25 | 726.3
Diesel fuel oil 20 to 60 | 15 | 820 - 950
Diethyl ether | 20 | 714
o-Dichlorobenzene | 20 | 1306
Dichloromethane | 20 | 1326
Diethylene glycol | 15 | 1120
Dichloromethane | 20 | 1326
Dimethyl Acetamide | 20 | 942
N,N-Dimethylformamide | 20 | 949
Dimethyl Sulfoxide | 20 | 1100
Dodecane | 25 | 754.6
Ethane | -89 | 570
Ether | 25 | 713.5
Ethylamine | 16 | 681
Ethyl Acetate | 20 | 901
Ethyl Alcohol | 20 | 789
Ethyl Ether | 20 | 713
Ethylene Dichloride | 20 | 1253
Ethylene glycol | 25 | 1097
Freon (Fluorine) refrigerant R-11 | 25 | 1476
Fluorine refrigerant R-12 | 25 | 1311
Fluorine refrigerant R-22 | 25 | 1194
Formaldehyde | 45 | 812
Formic acid 10%oncentration | 20 | 1025
Formic acid 80%oncentration | 20 | 1221
Freon - 11 | 21 | 1490
Freon - 21 | 21 | 1370
Fuel oil | 60oF | 890
Furan | 25 | 1416
Furforol | 25 | 1155
Gasoline, natural | 60oF | 711
Gasoline, Vehicle | 60oF | 737
Gas oils | 60oF | 890
Glucose | 60oF | 1350 - 1440
Glycerine | 25 | 1259
Glycerol | 25 | 1126
Heating oil | 20 | 920
Heptane | 25 | 679.5
Hexane | 25 | 654.8
Hexanol | 25 | 811
Hexene | 25 | 671
Hydrazine | 25 | 795
Iodine | 25 | 4927
Ionene | 25 | 932
Isobutyl Alcohol | 20 | 802
Iso-Octane | 20 | 692
Isopropyl Alcohol | 20 | 785
Isopropyl Myristate | 20 | 853
Kerosene | 60oF | 820.1
Linolenic Acid | 25 | 897
Linseed oil | 25 | 929.1
Machine oil | 20 | 910
Mercury |  | 13590
Methane | -164 | 465
Methanol | 20 | 791
Methyl Isoamyl Ketone | 20 | 888
Methyl Isobutyl Ketone | 20 | 801
Methyl n-Propyl Ketone | 20 | 808
Methyl t-Butyl Ether | 20 | 741
N-Methylpyrrolidone | 20 | 1030
Methyl Ethyl Ketone | 20 | 805
Milk | 15 | 1020 - 1050
Naphtha | 15 | 665
Naphtha, wood | 25 | 960
Napthalene | 25 | 820
Nitric acid | 0 | 1560
Ocimene | 25 | 798
Octane | 15 | 698.6
Oil of resin | 20 | 940
Oil of turpentine | 20 | 870
Oil, lubricating | 20 | 900
Olive oil | 20 | 800 - 920
Oxygen (liquid) | -183 | 1140
Paraffin |  | 800
Palmitic Acid | 25 | 851
Pentane | 20 | 626
Pentane | 25 | 625
Perchlor ethylene | 20 | 1620
Petroleum Ether | 20 | 640
Petrol, natural | 60oF | 711
Petrol, Vehicle | 60oF | 737
Phenol | 25 | 1072
Phosgene | 0 | 1378
Phytadiene | 25 | 823
Pinene | 25 | 857
Propane | -40 | 493.5
Propane, R-290 | 25 | 494
Propanol | 25 | 804
Propylenearbonate | 20 | 1201
Propylene | 25 | 514.4
Propylene glycol | 25 | 965.3
Pyridine | 25 | 979
Pyrrole | 25 | 966
Rape seed oil | 20 | 920
Resorcinol | 25 | 1269
Rosin oil | 15 | 980
Sea water | 25 | 1025
Silane | 25 | 718
Silicone oil |  | 760
Sodium Hydroxide (caustic soda) | 15 | 1250
Sorbaldehyde | 25 | 895
Soya bean oil | 15 | 924 - 928
Stearic Acid | 25 | 891
Sulfuric Acid 95%onc. | 20 | 1839
Sulfurus acid | -20 | 1490
Sugar solution 68 brix | 15 | 1338
Sunflower oil | 20 | 920
Styrene | 25 | 903
Terpinene | 25 | 847
Tetrahydrofuran | 20 | 888
Toluene | 20 | 867
Trichlor ethylene | 20 | 1470
Triethylamine | 20 | 728
Trifluoroacetic Acid | 20 | 1489
Turpentine | 25 | 868.2
Water, heavy | 11.6 | 1105
Water - pure | 4 | 1000
Water - sea | 77oF | 1022
Whale oil | 15 | 925
o-Xylene | 20 | 880